# Modbus RTU Protocol

#### Administrator 2025/3/13

Shenzhen Lux Power Technology Co., Ltd	www.luxpowertek.com

|  | Version | Changes | Date of change | Responsible person | Remark |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | V00 | First version | 2024.02.23 |  |  |  |
|  | V01 | Definition modifications on Hold reg19 and Hold reg 20. Add Hold 21 register as the Permit Service function. | 2024.04.24 | Mason Chloe |  |  |
|  | V02 | - Add Hold233 uFuntion4. DryContactorMultiplex bit4-7,Select dry contact multiplexing function ; - Add Input206、207，AC couple power for S- phase and T-phase （TriP 6-20K）; - Add Hold248~251,CT ratio and direction for WattNode meter - Add Hold233 uFuntion4 .uExCTPosition bit8-9 External power grid CT settings - Add Hold252 Used for NEC120% Rule BusBar current limiting setting - Add Hold110 CTSampleRatio、 PVCTSampleRatio - Add Hold233 Bit10 ：EN50549 F-stop opening and closing of over frequency load shedding logic Added hold253: DeltaSOC, used to set the hysteresis of battery SOC - Added hold254: DeltaVolt, used to set the hysteresis of the battery Volt - Add hold120 bit8：SeparateZeroExportEn - Add Rule 24(TOR),25(Denmark DK2) （TriP 6- 20K） 10. Add hold255 Bit3-7 Used to read WattNode meter frequency | 2024.10.16 | JiaLuo |  |  |
|  | V03 | - Add input214, input215, and input216 to store three temperatures - Add input217-231 to store the voltage and power, daily energy, and total energy of PV4-PV6 - Add an option in bit 1 - 3 of hold 120 for 12K: AC charging Enable bit (both time period and SOC/Volt are required); - Add hold 256 - 259 to store Generator start time and end time; - Added input232,used to display Smart load power - Add input210,Remaining seconds of one click charging process - For 12K, Change the CT ratio setting bits 5-6 and 12-13 of hold110 to CTSampleRatioL2 and CTSampleRatioH2, and merge them into a 4-bit CTSampleRatio to increase the CT ratio option settings. - Add the Input174 register Bit10 as a flag to indicate whether the generator quick start function is displayed - Add hold260 as the alarm voltage setting value for BUS overvoltage point - Add input176、177、178 to display the historical events of three-phase ExceptionReason1, ExceptionReason2, ChgDischgDisabReason; - Add Trip_LV low-voltage LCD11 to the LCD coding definition - New Hold261 register: Recovery discharge threshold setting register (including voltage and SOC). The recovery of battery low warning point, off grid discharge cut-off point, and grid connected discharge cut-off point will all share the same | 2025.3.13 | JiaLuo |  |  |

threshold. Discharge recovery point=discharge cut- off point+discharge recovery threshold

Directory

- Introduction to the Modbus RTU protocol	3

- Message Format	3

- Byte Order	3

- Requests and Responses	3

- Communication Configuration	7

- Register Mapping Table	8

- Input Register	8

- Hold Register	17

- Appendix	34

- Definition of the operation mode of on/off energy storage all in one machine . 34

- Fault and Alarm Code Definitions	35

- On-grid Regulatory Mapping Table	40

- LCD Definition Table	40

Shenzhen Lux Power Technology Co., Ltd	www.luxpowertek.com

2 / 41

c

# Introduction to the Modbus RTU protocol

## Message Format

| Address | Function Code | Data | CRC checksum |  |
| --- | --- | --- | --- | --- |
| 1 byte | 1 byte | 1-252 byte | Low byte | High byte |

Table 1 Message Format

The Modbus protocol utilizes several function codes, including:

Function Code 0x03: Read Holding Registers Function Code 0x04: Read Input Registers Function Code 0x06: Write Single Holding Register

Function Code 0x10: Write Multiple Holding Registers

## Byte Order

| Start bit | Data |  |  |  |  |  |  |  | Stop bit |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | Bit0 | Bit1 | Bit2 | Bit3 | Bit4 | Bit5 | Bit6 | Bit7 | 1 |

Table 2 Byte Order

## Requests and Responses

### Responses include normal responses and exception responses, the exception codes are defined as follows:

| Exception code | Description of the exception | Remark |
| --- | --- | --- |
| 0x01 | Illegal Function | Secondary does not recognize the function code |
| 0x02 | Illegal Data Address | The data address does not match the length |
| 0x03 | Illegal Data Value | The data value is out of bounds or the number of registers is incorrect |
| 0x04 | Secondary read and write failed | Read and write errors |
| 0x06 | Secondary Busy | Secondary busy |

Table 3 Exception Code Definitions

### Read the hold and input registers

| Request | Normal Response | Exception Response |
| --- | --- | --- |
| Address | Address | Address |
| Function code(0x03/0x04） | Function Code(0x03/0x04） | Function Code(0x83/0x84) |
| SN[0] | SN[0] | SN[0] |
| SN[1] | SN[1] | SN[1] |
| SN[2] | SN[2] | SN[2] |
| SN[3] | SN[3] | SN[3] |
| SN[4] | SN[4] | SN[4] |
| SN[5] | SN[5] | SN[5] |
| SN[6] | SN[6] | SN[6] |
| SN[7] | SN[7] | SN[7] |
| SN[8] | SN[8] | SN[8] |
| SN[9] | SN[9] | SN[9] |
| Start address A low byte | Start address A low byte | Start address A low byte |
| Start address A high byte | Start address A high byte | Start address A high byte |
| Number of registers N low bytes | Number of bytes | Exception code |
| Number of registers N high bytes | Register A value is low byte | CRC checks low bytes |
| CRC checks low bytes | Register A value high bytes | CRC checks high bytes |
| CRC checks high bytes | Register A+1 value low bytes |  |
|  | Register A+1 value high bytes |  |
|  | …… |  |
|  | …… |  |
|  | Register A+N-1 value low bytes |  |
|  | Register A+N-1 value high bytes |  |
|  | CRC checks low bytes |  |
|  | CRC checks high bytes |  |

Table 4 Read Requests and Responses

### Write a single hold register

| Request | Normal Response | Exception Response |
| --- | --- | --- |
| Address | Address | Address |
| Function Code(0x06） | Function Code(0x06） | Function Code(0x86) |
| SN[0] | SN[0] | SN[0] |
| SN[1] | SN[1] | SN[1] |
| SN[2] | SN[2] | SN[2] |
| SN[3] | SN[3] | SN[3] |
| SN[4] | SN[4] | SN[4] |
| SN[5] | SN[5] | SN[5] |
| SN[6] | SN[6] | SN[6] |
| SN[7] | SN[7] | SN[7] |
| SN[8] | SN[8] | SN[8] |
| SN[9] | SN[9] | SN[9] |
| Register address low byte | Register address low byte | Register address low byte |
| Register address high bytes | Register address high bytes | Register address high bytes |
| Register value low byte | Register value low byte | Exception code |
| Register value high bytes | Register value high bytes | CRC checks low bytes |
| CRC checks low bytes | CRC checks low bytes | CRC checks high bytes |
| CRC checks high bytes | CRC checks high bytes |  |

Table 5 Writing Individual Registers and Responses

### Write multiple hold registers

| Request | Normal Response | Exception Response |
| --- | --- | --- |
| Address | Address | Address |
| Function Code(0x10) | Function Code(0x10) | Function Code(0x90) |
| SN[0] | SN[0] | SN[0] |
| SN[1] | SN[1] | SN[1] |
| SN[2] | SN[2] | SN[2] |
| SN[3] | SN[3] | SN[3] |

| SN[4] | SN[4] | SN[4] |
| --- | --- | --- |
| SN[5] | SN[5] | SN[5] |
| SN[6] | SN[6] | SN[6] |
| SN[7] | SN[7] | SN[7] |
| SN[8] | SN[8] | SN[8] |
| SN[9] | SN[9] | SN[9] |
| Start address A low byte | Start address A low byte | Start address A low byte |
| Start address A high byte | Start address A high byte | Start address A high byte |
| Number of registers N low bytes | Number of registers N low bytes | Exception code |
| Number of registers N high bytes | Number of registers N high bytes | CRC checks low bytes |
| Number of bytes | CRC checks low bytes | CRC checks high bytes |
| Register A value low bytes | CRC checks high bytes |  |
| Register A value high bytes |  |  |
| Register A+1 value low bytes |  |  |
| Register A+1 value high bytes |  |  |
| …… |  |  |
| …… |  |  |
| Register A+N-1 value low bytes |  |  |
| Register A+N-1 value high bytes |  |  |
| CRC checks low bytes |  |  |
| CRC checks high bytes |  |  |

Table 6 Writing Multiple Registers and Responses

# Communication Configuration

  - Physical interface: RS-485

  - Communication mode: Universal asynchronous transceiver (UART)

  - Baud rate: 19200bps

  - One start bit, 8 data bits, no parity bits, one stop bit, total 10 bytes.

  - Minimum polling period: 1s

  - Register width: 2 bytes

  - 16-bit integer decoding order: The high and low byte order is reversed, for example 0x01 0x02, it should be parsed as 0x0201=513

  - 32-bit integer decoding order: The high and low byte order is reversed, the byte sequence within the word reversed, for example 0x01 0x02 0x03 0x04, should be parsed as 0x04030201=67305985

  - A maximum of 40 registers can be queried in a single request. The inverter software groups the registers in sets of 40, starting from 0-39 for the first group, 40-79 for the second group, 80-119 for the third group, and so on. When querying 40 registers, the starting address must be 0 (0-39), 40 (40-79), 80 (80-119), and so on. It is not allowed to query registers that span across different groups simultaneously. For example, if you need to query the values of

registers 38-40, you must perform two separate queries because 38-39 are in the first group and 40 is in the second group.

  - The maximum number of registers that can be queried in a single request for the new inverter is 127.

# Register Mapping Table

## Input Register

### It is used to store the operational data of the energy storage inverter, which can only be read and not written, and supports function codes 0x04.

| Input Addr | Item | Unit | Range | Note |
| --- | --- | --- | --- | --- |
| 0 | State |  | 0-65535 | For more information,see the definition of the operation mode of off-grid-connected energy storage all- in-one file |
| 1 | Vpv1 | 0.1V | 0-65535 | PV1 voltage, the AC energy storage system does not have this variable |
| 2 | Vpv2 | 0.1V | 0-65535 | PV2 voltage, the AC energy storage system does not have this variable |
| 3 | Vpv3 | 0.1V | 0-65536 | PV3 voltage, the AC energy storage system does not have this variable |
| 4 | Vbat | 0.1V | 0-65535 | Battery voltage |
| 5 | SOC | % | 0-100 | Battery capacity |
|  | SOH | % | 0-100 | Battery State of health |
| 6 | Internal Fault |  | 0-65535 | For more information, see Internal Fault Code Definition file |
| 7 | Ppv1 | W | 0-65535 | PV1 power/ AC energy storage Ppv |
| 8 | Ppv2 | W | 0-65535 | PV2 power, the AC energy storage system does not have this variable |
| 9 | Ppv3 | W | 0-65536 | PV3 power (total PV power, obtained by adding PV1, 2, 3), the AC energy storage system does not have this variable |
| 10 | Pcharge | W | 0-65535 | Charging power (power flowing into the battery) |
| 11 | Pdischarge | W | 0-65535 | Discharging power (power flowing out of battery power) |
| 12 | VacR | 0.1V | 0-65535 | R-phase utility grid voltage |
| 13 | VacS | 0.1V | 0-65535 | S-phase utility grid voltage |
| 14 | VacT | 0.1V | 0-65535 | T-phase utility grid voltage |
| 15 | Fac | 0.01Hz | 0-65535 | Utility grid frequency |
| 16 | Pinv | W | 0-65535 | On-gird inverter power (For three phase: R phase) |
| 17 | Prec | W | 0-65535 | AC charging rectification power (For three phase: R phase) |
| 18 | IinvRMS | 0.01A | 0-65535 | Inverter rms current output (For three phase: R phase) |
| 19 | PF | 0.001 | 0-2000 | Power factor xє(0,1000]->x/1000 xє(1000,2000)->(1000-x)/1000 (For three phase: R phase) |
| 20 | VepsR | 0.1V | 0-65535 | R phase off-grid output voltage |
| 21 | VepsS | 0.1V | 0-65535 | S phase off-grid output voltage |
| 22 | VepsT | 0.1V | 0-65535 | T phase off-grid output voltage |

| 23 | Feps | 0.01Hz | 0-65535 | Off-grid output frequency |
| --- | --- | --- | --- | --- |
| 24 | Peps | W | 0-65535 | Off-grid inverter power (For three phase: R phase) |
| 25 | Seps | VA | 0-65535 | Off-grid apparent power (For three phase: R phase) |
| 26 | Ptogrid | W | 0-65535 | User on-grid power (For three phase: R phase) |
| 27 | Ptouser | W | 0-65535 | Grid power capacity (For three phase: R phase) |
| 28 | Epv1_day | 0.1kWh | 0-65535 | PV1 power generation today / AC Energy Storage Epv_day |
| 29 | Epv2_day | 0.1kWh | 0-65535 | PV2 power generation today, the AC energy storage system does not have this variable |
| 30 | Epv3_day | 0.1kWh | 0-65535 | PV3 power generation today (total PV=PV1+PV2+PV3), the AC energy storage system does not have this variable |
| 31 | Einv_day | 0.1kWh | 0-65535 | Today's on-grid inverter output energy |
| 32 | Erec_day | 0.1kWh | 0-65535 | Today's AC charging rectifier energy |
| 33 | Echg_day | 0.1kWh | 0-65535 | Energy Charge today |
| 34 | Edischg_day | 0.1kWh | 0-65535 | Energy Discharge today |
| 35 | Eeps_day | 0.1kWh | 0-65535 | Today's off-grid output energy |
| 36 | Etogrid_day | 0.1kWh | 0-65535 | Today's export to gird energy |
| 37 | Etouser_day | 0.1kWh | 0-65535 | Electricity supplied to user from the grid today |
| 38 | Vbus1 | 0.1V | 0-65535 | Voltage of Bus 1 |
| 39 | Vbus2 | 0.1V | 0-65535 | Voltage of Bus 2 |
| 40 | Epv1_all L | 0.1kWh | 0-65535 | PV1 cumulative power generation/AC energy storage Epv_all Low byte |
| 41 | Epv1_all H | 0.1kWh | 0-65535 | PV1 cumulative power generation/AC energy storage Epv_all high byte |
| 42 | Epv2_all L | 0.1kWh | 0-65535 | PV2 cumulative power generation low byte, AC energy storage does not have this variable |
| 43 | Epv2_all H | 0.1kWh | 0-65535 | PV2 cumulative power generation high byte, AC energy storage does not have this variable |
| 44 | Epv3_all L | 0.1kWh | 0-65535 | PV3 cumulative power generation low byte (total PV=PV1+PV2+PV3), AC energy storage does not have this variable. |
| 45 | Epv3_all H | 0.1kWh | 0-65535 | PV3 cumulative power generation high byte (total PV=PV1+PV2+PV3), AC energy storage does not have this variable |
| 46 | Einv_all L | 0.1kWh | 0-65535 | Inverter output accumulated power low byte |

| 47 | Einv_all H | 0.1kWh | 0-65535 | Inverter output accumulates power high byte |
| --- | --- | --- | --- | --- |
| 48 | Erec_all L | 0.1kWh | 0-65535 | AC charging accumulates rectified power Low byte |
| 49 | Erec_all H | 0.1kWh | 0-65535 | AC charging accumulates rectified power high byte |
| 50 | Echg_all L | 0.1kWh | 0-65535 | Cumulative charge energy low byte |
| 51 | Echg_all H | 0.1kWh | 0-65535 | Cumulative charge energy high byte |
| 52 | Edischg_all L | 0.1kWh | 0-65535 | Cumulative discharge charge energy Low byte |
| 53 | Edischg_all H | 0.1kWh | 0-65535 | Cumulative discharge charge energy High byte |
| 54 | Eeps_all L | 0.1kWh | 0-65535 | Cumulative inverter off-grid output energy Low byte |
| 55 | Eeps_all H | 0.1kWh | 0-65535 | Cumulative inverter off-grid output energy High byte |
| 56 | Etogrid_all L | 0.1kWh | 0-65535 | Accumulate export energy Low byte |
| 57 | Etogrid_all H | 0.1kWh | 0-65535 | Accumulate export energy High byte |
| 58 | Etouser_all L | 0.1kWh | 0-65535 | Cumulative import energy Low byte |
| 59 | Etouser_all H | 0.1kWh | 0-65535 | Cumulative import energy high byte |
| 60 | FaultCode L |  | 0-65535 | For more information, see Fault code definition file |
| 61 | FaultCode H |  | 0-65535 | For more information, see Fault code definition file |
| 62 | WarningCode L |  | 0-65535 | For more information, see Alarm code definition file |
| 63 | WarningCode H |  | 0-65535 | For more information, see Alarm code definition file |
| 64 | Tinner | celsius | 0-65535 | Internal temperature |
| 65 | Tradiator1 | Celsius | 0-65535 | Radiator temperature 1 |
| 66 | Tradiator2 | celsius | 0-65535 | Radiator temperature 2 |
| 67 | Tbat | celsius | 0-65535 | Battery temperature |
| 69 | RunningTime L | second |  | Runtime duration |
| 70 | RunningTime H | second |  | Runtime duration |
| 71 | AutoTestStart | Bit0-3 |  | - - not started ; - - started |
|  | UbAutoTestStatus | Bit4-7 |  | 0-waiting 1-testing 2-test fail 3-V test OK 4-F test OK 5- test pass |
|  | UbAutoTestStep | Bit8-11 |  | 1-V1L test 2-V1H 3-F1L test 4-F1H test |

- V2L test

- V2H test

- F2L test

- F2H test

- wAutoTestLimit

- uwAutoTestDefault Time

- uwAutoTestTripValue

- uwAutoTestTripTime ACInputType

77	ACCoupleInverterFlow ACCoupleEn On SmartLoadFlow

SmartLoadEnOn

EpsLoadPowerShow

GridLoadPowerShow

PloadPowerShow

BatTypeAndBrand

#### 80

BatComType

- MaxChgCurr

- MaxDischgCurr

- ChargeVoltRef

0.1V/0.

01Hz

ms 0.1V/0.

01Hz

ms Bit0

Bit1 Bit2 Bit3

Bit4

Bit5

Bit6

Bit7

0.01A

0.01A

0.1V

0	or 1

0 or 1

0 or 1

0 or 1

0 or 1

0 or 1

0 or 1

0 or 1

0	or 1

When ubAuto Test Step=1,2,5,6, is the voltage limit;

When ubAutoTest Step=3,4,7,8, it is the frequency limit

When ubAuto Test Step=1,2,5,6, is the voltage limit;

When ubAutoTestStep=3,4,7,8, it is the frequency limit

0-Grid

1-Generator for 12KHybrid

0-no flow

1-show flow

0-Disable 1-Enable

0-no flow	1-show flow

When Bit4 is 1 and smartload power>0, set it to 1; Used to monitor the power arrow displayed on the homepage;

0-Disable	1-Enable Set to 1 when the user enables SmartLoad and the machine has reached the activation condition; Display power;

0-no power display	1-power display Temporarily set to 1 during initialization for compatibility with new and old software; Monitor whether the EPS side load power is displayed based on this flag

0-no power display	1-power display Temporarily set to 1 during initialization for compatibility with new and old software; Monitor whether the Grid side load power is displayed based on this flag

0-no power display	1-power display Temporarily set to 1 during initialization for compatibility with new and old software;Monitor whether to display the total load power based on the flag position

For more information, see the model definition file

0-CAN

1-485

The maximum charging current of BMS limits

The maximum discharging current of BMS limits

Recommends charging voltage by

Shenzhen Lux Power Technology Co., Ltd

BMSwww.luxpowertek.com

- DischgCutVolt

- BatStatus0_BMS

- BatStatus1_BMS

0.1V

11 / 41

Recommends a discharging cut-off voltage by BMS

Status information of BMS Status information of BMS

|  | 87 | BatStatus2_BMS |  |  | Status information of BMS |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | 88 | BatStatus3_BMS |  |  | Status information of BMS |  |
|  | 89 | BatStatus4_BMS |  |  | Status information of BMS |  |
|  | 90 | BatStatus5_BMS |  |  | Status information of BMS |  |
|  | 91 | BatStatus6_BMS |  |  | Status information of BMS |  |
|  | 92 | BatStatus7_BMS |  |  | Status information of BMS |  |
|  | 93 | BatStatus8_BMS |  |  | Status information of BMS |  |
|  | 94 | BatStatus9_BMS |  |  | Status information of BMS |  |
|  | 95 | BatStatus_INV |  |  | The inverter aggregates lithium battery status information |  |
|  | 96 | BatParallelNum |  |  | Number of batteries in parallel |  |
|  | 97 | BatCapacity | Ah |  | Battery capacity |  |
|  | 98 | BatCurrent_BMS | 0.01A |  | Battery current , with signed number |  |
|  | 99 | FaultCode_BMS |  |  |  |  |

| 100 | WarningCode_BMS |  |  |  |
| --- | --- | --- | --- | --- |
| 101 | MaxCellVolt_BMS | 0.001V |  | Maximum voltage of cell |
| 102 | MinCellVolt_BMS | 0.001V |  | Minimum voltage of cell |
| 103 | MaxCellTemp_BMS | 0.1℃ |  | Maximum temperature of cell, with signed number |
| 104 | MinCellTemp_BMS | 0.1℃ |  | Minimum temperature of cell, with signed number |
| 105 | BMSFWUpdateState |  | 1-3 | - Upgrade in process - Upgrade successful - Upgrade failed |
| 106 | CycleCnt_BMS |  |  | Number of charging/discharging cycles |
| 107 | BatVoltSample_INV | 0.1V |  | Tnverter samples the battery voltage |
| 108 | T1 | 0.1℃ |  | BT temperature for 12k |
| 109 | T2 | 0.1℃ |  | Reserved |
| 110 | T3 | 0.1℃ |  | Reserved |
| 111 | T4 | 0.1℃ |  | Reserved |
| 112 | T5 | 0.1℃ |  | Reserved |
| 113 | MasterOrSlave | Bit0~1 | 1,2 | Master or Slave 1: Master 2: Slave |
|  | SingleOrThreePhase | Bit2~3 | 1-3 | Parallel phase 1:R 2:S 3:T |
|  | Phases sequence | Bit4~5 | 0-1 | - Positive order - Negative order |
|  | Rsvd | Bit6~7 |  | Reserved |
|  | ParallelNum | Bit8~16 | 1~255 | Number of inverters in parallel |
| 114 | OnGridloadPower | W |  | Load power of the 12k inverter when it is not off-grid |
|  | SN[0]-Year |  | '0'-'9' 'A'- | The serial number is a ten-digit ASCII code For example: The serial number is AB12345678 SN[0]=0x41(A) : : : : SN[9]=0x38(8) www.luxpowertek.com |
| 115 |  |  | 'Z' |  |
|  | SN[1]-week |  |  |  |
|  |  |  | '0'-'9' 'A'- |  |
|  |  |  | 'Z' |  |
|  | SN[2]-week |  | '0'-'9' 'A'- |  |
| 116 |  |  | 'Z' |  |
|  | SN[3]-factory |  |  |  |
|  |  |  | '0'-'9' 'A'- |  |
|  |  |  | 'Z' |  |
|  | SN[4]-product code |  | '0'-'9' 'A'- |  |
| 117 |  |  | 'Z' |  |
|  | SN[5] -product code er Technology Co., Ltd |  |  |  |
|  |  |  | '0'-'9' 'A'- |  |
| Shenzhen Lux Pow |  |  | 'Z' |  |

12 / 41

| 118 | SN[6] -serial number |  | '0'-'9' 'A'- 'Z' |  |
| --- | --- | --- | --- | --- |
|  | SN[7]-serial number |  | '0'-'9' 'A'- 'Z' |  |
| 119 | SN[8] -serial number |  | '0'-'9' 'A'- 'Z' |  |
|  | SN[9] -serial number |  | '0'-'9' 'A'- 'Z' |  |
| 120 | VBusP | 0.1V |  | Half BUS voltage |
| 121 | GenVolt | 0.1V |  | Generator voltage Voltage of generator for three phase: R phase |
| 122 | GenFreq | 0.01Hz |  | Generator frequency |
| 123 | GenPower | W |  | Voltage of generator for three phase: R phase |
| 124 | Egen_day | 0.1kWh |  | Energy of generator today |
| 125 | Egen_all L | 0.1kWh |  | Low byte of total generator energy |
| 126 | Egen_all H | 0.1kWh |  | High byte of total generator energy |
| 127 | EPSVoltL1N | 0.1V |  | Voltage of EPS L1N Voltage of generator for three phase: S phase |
| 128 | EPSVoltL2N | 0.1V |  | Voltage of EPS L2N Voltage of generator for three phase: T phase |
| 129 | Peps_L1N | W |  | Active power of EPS L1N Off-grid active power of three phase: S phase |
| 130 | Peps_L2N | W |  | Active power of EPS L2N Off-grid active power of three phase: T phase |
| 131 | Seps_L1N | VA |  | Apparent power of EPS L1N Off-grid apparent power of three phase: S phase |
| 132 | Seps_L2N | VA |  | Apparent power of EPS L2N Off-grid apparent power of three phase: T phase |
| 133 | EepsL1N_day | 0.1kWh |  | Daily energy of EPSL1N Off-grid daily energy of three phase: S phase |
| 134 | EepsL2N_day | 0.1kWh |  | Daily energy of EPSL2N Off-grid daily energy of three phase: T phase |
| 135 | EepsL1N_all L | 0.1kWh |  | Low byte of total EPSL1N energy Total off-grid power of three phase: S phase |
| 136 | EepsL1N_all H | 0.1kWh |  | High byte of total EPSL1N energy Total off-grid power of three cameras: S phase |
| 137 | EepsL2N_all L | 0.1kWh |  | Low word of total EPSL2N energy Total off-grid power of three phase: T phase |

Shenzhen Lux Power Technology Co., Ltd	www.luxpowertek.com

|  | 138 | EepsL2N_all H | 0.1kWh |  | High byte of total EPSL2N energy Total off-grid power of three byte: T phase |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | 139 | Qinv | Var |  | Reactive power |  |
|  | 140 | AFCI_CurrCH1 | mA |  | AFCI current |  |
|  | 141 | AFCI_CurrCH2 | mA |  | AFCI current |  |
|  | 142 | AFCI_CurrCH3 | mA |  | AFCI current |  |
|  | 143 | AFCI_CurrCH4 | mA |  | AFCI current |  |
|  | 144 | AFCIFlag.ArcAlarmCH1 | Bit0 |  | Arc status of CH1 0-Normal 1-Alarm |  |
|  |  | AFCIFlag.ArcAlarmCH2 | Bit1 |  | Arc status of CH2 0-Normal 1-Alarm |  |
|  |  | AFCIFlag.ArcAlarmCH3 | Bit2 |  | Arc status of CH3 0-Normal 1-Alarm |  |
|  |  | AFCIFlag.ArcAlarmCH4 | Bit3 |  | Arc status of CH4 0-Normal 1-Alarm |  |
|  |  | AFCIFlag.SelfTestResult CH1 | Bit4 |  | Test result of CH1 0-Normal 1-fail |  |
|  |  | AFCIFlag.SelfTestResult CH2 | Bit5 |  | Test result of CH2 0-Normal 1-fail |  |
|  |  | AFCIFlag.SelfTestResult CH3 | Bit6 |  | Test result of CH3 0-Normal 1-fail |  |
|  |  | AFCIFlag.SelfTestResult CH4 | Bit7 |  | Test result of CH4 0-Normal 1-fail |  |
|  |  | AFCI_ArcAlarm.rsvd | Bit8-15 |  |  |  |
|  | 145 | AFCI_ArcCH1 |  |  | Real time arc of CH1 |  |
|  | 146 | AFCI_ArcCH2 |  |  | Real time arc of CH2 |  |
|  | 147 | AFCI_ArcCH3 |  |  | Real time arc of CH3 |  |
|  | 148 | AFCI_ArcCH4 |  |  | Real time arc of CH4 |  |
|  | 149 | AFCI_MaxArcCH1 |  |  | Max arc of CH1 |  |
|  | 150 | AFCI_MaxArcCH2 |  |  | Max arc of CH2 |  |
|  | 151 | AFCI_MaxArcCH3 |  |  | Max arc of CH3 |  |
|  | 152 | AFCI_MaxArcCH4 |  |  | Max arc of CH4 |  |
|  | 153 | ACCouplePower | W |  | AC Coupled inverter power |  |
|  | 154 | AutoTestTripValue[0] | 0.1V/0. 01Hz |  |  |  |
|  | …… |  |  |  |  |  |
|  | 161 | AutoTestTripValue[7] | 0.1V/0. 01Hz |  |  |  |
|  | 162 | AutoTestTripTime [0] | ms |  |  |  |
|  | …… |  |  |  |  |  |
|  | 169 | AutoTestTripTime [7] | ms |  |  |  |
|  | 170 | Pload | W |  | Load consumption when working in on-grid mode |  |
|  | 171 | Eload_day | 0.1kWh |  | Load energy for today |  |
|  | 172 | Eload_allL | 0.1kWh |  | Load energy for total High byte |  |
|  | 173 | Eload_allH | 0.1kWh |  | Load energy for total Low byte |  |
|  | 174 | SwitchState.SafetySw | Bit0~4 | 0~0x1F | The status of the 5-digit safety DIP switch |  |
|  |  | SwitchState.rsvd | Bit5-7 | 0 | Reserved |  |
|  |  | SwitchState.EpsSwOn | Bit8 |  | Status of EPS switch |  |
|  |  | SwitchState.DrySwOn | Bit9 |  | Generator dry contact status |  |
|  |  | SwitchState.GenQuick StartUsed | Bit10 |  | generator quick start flag displayed |  |
|  |  | SwitchState.rsvd | Bit11-14 |  | Reserved |  |
|  |  | SwitchState.SwRegUsed | Bit15 |  | Determine whether the switch register is being used |  |
|  | 175 | EPS overload ctrl time | s |  | Connect in xx S after triggering the EPS overload issue |  |

|  | 176 | ExceptionReason1 | Bit0~3 |  | 3phase:PVGridOn Exit Reason |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Bit4~7 |  | 3phase:PVChgGridOn Exit Reason |  |
|  |  |  | Bit8~11 |  | 3phase:BatGridOn Exit Reason |  |
|  |  |  | Bit12~1 5 |  | 3phase:PVBatGridOn Exit Reason |  |
|  | 177 | ExceptionReason2 | Bit0~3 |  | 3phase:PVCharge Exit Reason |  |
|  |  |  | Bit4~7 |  | 3phase:ACCharge Exit Reason |  |
|  |  |  | Bit8~11 |  | 3phase:PVACCharge Exit Reason |  |
|  |  |  | Bit12~1 5 |  | 3phase:EPS Exit Reason |  |
|  | 178 | ChgDischgDisableReaso n | Bit0~7 |  | 3phase:Charge Exit Reason |  |
|  |  |  | Bit8~15 |  | 3phase:Discharge Exit Reason |  |
|  | …… | …… | …… | …… | …… |  |
|  | 180 | Pinv_S | W | 0-65535 | On grid inverter power of three phase: S phase |  |

|  | 181 | Pinv_T | W | 0-65535 | On grid inverter power of three phase: T phase |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | 182 | Prec_S | W | 0-65535 | Charging rectification power of three phase: S phase |  |
|  | 183 | Prec_T | W | 0-65535 | Charging rectification power of three phase: T phase |  |
|  | 184 | Ptogrid_S | W | 0-65535 | User on-grid power of three phase: S phase |  |
|  | 185 | Ptogrid_T | W | 0-65535 | User on-grid power of three phase: T phase |  |
|  | 186 | Ptouser_S | W | 0-65535 | Grid supply power of three phase: S phase |  |
|  | 187 | Ptouser_T | W | 0-65535 | Grid supply power of three phase:T phase |  |
|  | 188 | GenPower_S | W | 0-65535 | Power of generator for three phase: S phase |  |
|  | 189 | GenPower_T | W | 0-65535 | Power of generator for three phase: T phase |  |
|  | 190 | IinvRMS_S | 0.01 | 0-65535 | Effective value of three phase inverter current: S phase |  |
|  | 191 | IinvRMS_T | 0.01 | 0-65535 | Effective value of three phase inverter current: T phase |  |
|  | 192 | PF_S | 0.001 | 0-2000 | Power factor of phase S in three- phase inverter xє(0,1000]->x/1000 xє(1000,2000)->(1000-x)/1000 |  |
|  | 193 | GridVoltL1N | 0.1V |  | Voltage of Grid L1N （for US model） |  |
|  | 194 | GridVoltL2N | 0.1V |  | Voltage of Grid L2N（for US model） |  |
|  | 195 | GenVoltL1N | 0.1V |  | Voltage of Gen L1N（for US model） |  |
|  | 196 | GenVoltL2N | 0.1V |  | Voltage of Gen L2N（for US model） |  |
|  | 197 | PinvL1N | W | 0-65535 | Inverting power of phase L1N （for US model） |  |
|  | 198 | PinvL2N | W | 0-65535 | Inverting power of phase L2N （for US model） |  |
|  | 199 | PrecL1N | W | 0-65535 | Rectifying power of phase L1N （for US model） |  |
|  | 200 | PrecL2N | W | 0-65535 | Rectifying power of phase L2N （for US model） |  |
|  | 201 | Ptogrid_L1N | W | 0-65535 | Grid export power of phase L1N (for US model） |  |
|  | 202 | Ptogrid_L2N | W | 0-65535 | Grid export power of phase L2N (for US model） |  |
|  | 203 | Ptouser_L1N | W | 0-65535 | Grid import power of phase L1N (for US model） |  |
|  | 204 | Ptouser_L2N | W | 0-65535 | Grid import power of phase L2N (for US |  |

|  |  |  |  |  | model） |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | 205 | PF_T | 0.001 | 0-2000 | Power factor of phase T in three- phase inverter xє(0,1000]->x/1000 xє(1000,2000)->(1000-x)/1000 |  |
|  | 206 | ACCouplePower_S | W |  | AC Couple inverter power_S |  |
|  | 207 | ACCouplePower_T | W |  | AC Couple inverter power_T |  |
|  | 208 | OnGridloadPowerS | W |  | Load power of S-phase the Trip6-20k inverter when it is not off-grid |  |
|  | 209 | OnGridloadPowerT | W |  | Load power of T-phase the Trip6-20k inverter when it is not off-grid |  |
|  | 210 | Remaining seconds | S |  | Remaining seconds of one click charging process |  |
|  | ... |  |  |  |  |  |
|  | 214 | uwNTCForINDC | celsius | 0-65535 | Internal temperature |  |
|  | 215 | uwNTCForDCDCL | Celsius | 0-65535 | Radiator temperature 1 |  |
|  | 216 | uwNTCForDCDCH | celsius | 0-65535 | Radiator temperature 2 |  |
|  | 217 | Vpv4 | 0.1V | 0-65535 | PV4 voltage, the AC energy storage system does not have this variable |  |
|  | 218 | Vpv5 | 0.1V | 0-65535 | PV5 voltage, the AC energy storage system does not have this variable |  |
|  | 219 | Vpv6 | 0.1V | 0-65536 | PV6 voltage, the AC energy storage system does not have this variable |  |
|  | 220 | Ppv4 | W | 0-65535 | PV4 power, the AC energy storage system does not have this variable |  |
|  | 221 | Ppv5 | W | 0-65535 | PV5 power, the AC energy storage system does not have this variable |  |
|  | 222 | Ppv6 | W | 0-65535 | PV6 power, the AC energy storage system does not have this variable |  |
|  | 223 | Epv4_day | 0.1kWh | 0-65535 | PV4 power generation today, the AC energy storage system does not have this variable |  |
|  | 224 | Epv4_all L | 0.1kWh | 0-65535 | PV4 cumulative power generation low byte, AC energy storage does not have this variable |  |
|  | 225 | Epv4_all H | 0.1kWh | 0-65535 | PV4 cumulative power generation high byte, AC energy storage does not have this variable |  |
|  | 226 | Epv5_day | 0.1kWh | 0-65535 | PV5 power generation today, the AC energy storage system does not have this variable |  |
|  | 227 | Epv5_all L | 0.1kWh | 0-65535 | PV5 cumulative power generation low byte, AC energy storage does not have this variable |  |
|  | 228 | Epv5_all H | 0.1kWh | 0-65535 | PV5 cumulative power generation high byte, AC energy storage does not have this variable |  |
|  | 229 | Epv6_day | 0.1kWh | 0-65535 | PV6 power generation today, the AC energy storage system does not have this variable |  |
|  | 230 | Epv6_all L | 0.1kWh | 0-65535 | PV6 cumulative power generation low byte, AC energy storage does not have this variable |  |
|  | 231 | Epv6_all H | 0.1kWh | 0-65535 | PV6 cumulative power generation high byte, AC energy storage does not have this variable |  |
|  | 232 | Smart Load Power | W |  | Smart Load output power |  |
| Table 7 Input Register Mapping Table (Signed numbers indicated with a green background) |  |  |  |  |  |  |

# Hold Register

……

### It is used to store the operational data of the energy storage inverter, which can only be read and written, and supports function codes 0x03, 0x06, 0x10.

| Hold Addr | Item | Unit | Range and default | Note |
| --- | --- | --- | --- | --- |
| 7 | FWCode0 |  | 'A'-'Z' 'a'-'z' | For more information of the model code, see Software Version Definition file |
|  | FWCode1 |  | 'A'-'Z' 'a'-'z' | For more information of the code name for the derived model, see the software version definition file |
| 8 | FWCode2 |  | 'A'-'Z' 'a'-'z' | For more information of the ODM code,see Software Version Definition |
|  | FWCode3 |  | 'A'-'Z' 'a'-'z' | For more information of the region code, see Software Version Definition file |
| 9 | Slave Ver |  | 0-255 | For more information of the software version number for redundant CPU, see Software version definition file |
|  | Com Ver |  | 0-255 | For Communication CPU software version number, see software version definition file |
| 10 | Cntl Ver |  | 0-255 | For Control CPU software version number, see software version definition file |
|  | FWVer |  | 0-255 | For external software version number, see Software Version |

Shenzhen Lux Power Technology Co., Ltd	www.luxpowertek.com

17 / 41

|  | 11 | ... | Bit0 | 0/1 |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | ResetSetting.AlltoDefault | Bit1 | 0/1 | System settings restored to default values |  |
|  |  | ... | Bit2 | 0/1 |  |  |
|  |  | ... | Bit3 | 0/1 |  |  |
|  |  | ... | Bit4 | 0/1 |  |  |
|  |  | ... | Bit5 | 0/1 |  |  |
|  |  | ... | Bit6 | 0/1 |  |  |
|  |  | ResetSetting. InvReboot | Bit7 | 0/1 | 0-null 1- restart inverter |  |
|  |  | ResetSetting.rsvd | Bit8 | 0/1 | Retain |  |
|  |  | ResetSetting.rsvd | Bit9 | 0/1 | Retain |  |
|  |  | ResetSetting.rsvd | Bit10 | 0/1 | Retain |  |
|  |  | ResetSetting.rsvd | Bit11 | 0/1 | Retain |  |
|  |  | ResetSetting.rsvd | Bit12 | 0/1 | Retain |  |
|  |  | ResetSetting.rsvd | Bit13 | 0/1 | Retain |  |
|  |  | ResetSetting.rsvd | Bit14 | 0/1 | Retain |  |
|  |  | ResetSetting.rsvd | Bit15 | 0/1 | Retain |  |
|  | 12 | Time_Year |  | 17-255 | inverter time-year |  |
|  |  | Time_Month |  | 1-12 | inverter time-month |  |
|  | 13 | Time_Date |  | 1-31 | inverter time-day |  |
|  |  | Time_Hour |  | 0-23 | inverter time-hour |  |
|  | 14 | Time_Minute |  | 0-59 | inverter time-minute |  |
|  |  | Time_Second |  | 0-59 | inverter time-second |  |
|  | 15 | Com Addr |  | 0-150 | MODBUS address |  |
|  | 16 | Language |  | 0-1 | 0-English 1-German Language 0-English 1-German |  |
|  | 19 | DTC:Device type |  | 0-31 | 0： Default 3: XOLTA (for high-speed communication interval ) |  |
|  | 20 | PVInputModel | 1 | 0-4 For 12KHybrid:0-7 8 / 41 | 0: No PV plug in 1: PV1 plug in 2: PV2 plug in 3: two PVs in parallel 4: two separate PVs, AC energy storage does not have this variable. For 12KHybrid： - No PV - PV1 in - PV2 in - PV3 in - PV1&2 in - PV1&3 in - PV2&3 in 7-PV1&2&3 in For TriP 6-20k : - All MPPTs with individual PV strings - PV1&2 in parallel connection - PV1 & 3 in parallel connection 3 - PV2 and PV3 in parallel connection |  |

4 - PV1&2&3 in parallel connection

FuncEn.EPSEn	0

1

21	FuncEn.OVFLoadDerate

En

FuncEn.DRMSEn	2

0/1

0/1

0/1

Off-grid mode enable

Overfrequency load reduction enable

DRMS enable

|  | FuncEn.LVRTEn | 3 | 0/1 | Low voltage ride-through enable |
| --- | --- | --- | --- | --- |
|  | FuncEn.AntiIslandEn | 4 | 0/1 | Anti-islanding enablement |
|  | FuncEn.NeutralDetectE n | 5 | 0/1 | Ground neutral detection enable |
|  | FuncEn.GridOnPowerSS En | 6 | 0/1 | On-grid power soft start enable |
|  | FuncEn.ACChargeEn | 7 | 0/1 | AC charging enable |
|  | FuncEn.SWSeamlesslyE n | 8 | 0/1 | seamless off-grid mode switching enable |
|  | FuncEn.SetToStandby | 9 | 0/1 | 0: Standby 1: Power on |
|  | FuncEn.ForcedDischgEn | 10 | 0/1 | Forced discharge enable |
|  | FuncEn.ForcedChgEn | 11 | 0/1 | Force charge enable |
|  | FuncEn.ISOEn | 12 | 0/1 | ISO enable, and AC energy storage does not have this variable |
|  | FuncEn.GFCIEn | 13 | 0/1 | GFCI enable |
|  | FuncEn.DCIEn | 14 | 0/1 | DCI enable |
|  | FuncEn.FeedInGridEn | 15 | 0/1 | 0-disable 1-enable |
| 22 | StartPVVolt | 0.1V | 900-5000 | PV start-up voltage, AC energy storage does not have this variable |
| 23 | ConnectTime | s | 30-600 | Waiting time of on-grid |
| 24 | ReconnectTime | s | 0-900 | Waiting time of Reconnect on- gird |
| 25 | GridVoltConnLow | 0.1V | According to specific regulatory requirements | The lower limit of the allowed on-grid voltage. |
| 26 | GridVoltConnHigh | 0.1V | According to specific regulatory requirements | The upper limit of the the allowed on-grid voltage. |
| 27 | GridFreqConnLow | 0.01Hz | According to specific regulatory requirements | The lower limit of the allowable on-grid frequency |
| 28 | GridFreqConnHigh | 0.01Hz | According to specific regulatory requirements | The upper limit of the the allowed on-grid frequency. |
| 29 | GridVoltLimit1Low | 0.1V | According to specific regulatory requirements | Grid voltage level 1 undervoltage protection point |

| 30 | GridVoltLimit1High | 0.1V | According to specific regulatory requirements | Grid voltage level 1 overvoltage protection point |
| --- | --- | --- | --- | --- |
| 31 | GridVoltLimit1LowTime | Main period | According to specific regulatory requirements | Grid voltage level 1 undervoltage protection time |
| 32 | GridVoltLimit1HighTime | Main period | According to specific regulatory requirements | Grid voltage level 1 overvoltage protection time |
| 33 | GridVoltLimit2Low | 0.1V | According to specific regulatory requirements | Grid voltage level 2 undervoltage protection point |
| 34 | GridVoltLimit2High | 0.1V | According to specific regulatory requirements | Grid voltage level 2 overvoltage protection point |
| 35 | GridVoltLimit2LowTime | Main period | According to specific regulatory requirements | Grid voltage level 2 undervoltage protection time |
| 36 | GridVoltLimit2HighTime | Main period | According to specific regulatory requirements | Grid voltage level 2 overvoltage protection time |
| 37 | GridVoltLimit3Low | 0.1V | According to specific regulatory requirements | Grid voltage level 3 undervoltage protection point |
| 38 | GridVoltLimit3High | 0.1V | According to specific regulatory requirements | Grid voltage level 3 overvoltage protection point |
| 39 | GridVoltLimit3LowTime | Main period | According to specific regulatory requirements | Grid voltage level 3 undervoltage protection time |
| 40 | GridVoltLimit3HighTime | Main period | According to specific regulatory requirements | Grid voltage level 3 overvoltage protection time |
| 41 | GridVoltMovAvgHigh | 0.1V | According to specific regulatory | Grid voltage sliding average overvoltage protection point |

| 42 | GridFreqLimit1Low | 0.01Hz | requirements According to specific regulatory requirements | Grid frequency level 1 underfrequency protection point |
| --- | --- | --- | --- | --- |
| 43 | GridFreqLimit1High | 0.01Hz | According to specific regulatory requirements | Grid frequency level 1 overfrequency protection point |
| 44 | GridFreqLimit1LowTime | Main period | According to specific regulatory requirements | Grid frequency level 1 underfrequency protection time |
| 45 | GridFreqLimit1HighTime | Main period | According to specific regulatory requirements | Grid frequency level 1 overfrequency protection time |
| 46 | GridFreqLimit2Low | 0.01Hz | According to specific regulatory requirements | Grid frequency level 2 underfrequency protection point |
| 47 | GridFreqLimit2High | 0.01Hz | According to specific regulatory requirements | Power grid frequency level 2 overfrequency protection point |
| 48 | GridFreqLimit2LowTime | Main period | According to specific regulatory requirements | Grid frequency level 2 underfrequency protection time |
| 49 | GridFreqLimit2HighTime | Main period | According to specific regulatory requirements | Grid frequency level 2 overfrequency protection time |
| 50 | GridFreqLimit3Low | 0.01Hz | According to specific regulatory requirements | Grid frequency level 3 underfrequency protection point |
| 51 | GridFreqLimit3High | 0.01Hz | According to specific regulatory requirements | Grid frequency level 3 overfrequency protection point |
| 52 | GridFreqLimit3LowTime | Main period | According to specific regulatory requirements | Grid frequency level 3 underfrequency protection time |
| 53 | GridFreqLimit3HighTime | Main period | According to specific regulatory requirements | Grid frequency level 3 overfrequency protection time |

| 54 | MaxQPercentForQV | % | According to specific regulatory requirements | The maximum percentage of reactive power for the Q(V) curve |
| --- | --- | --- | --- | --- |
| 55 | V2L | 0.1V | According to specific regulatory requirements | Q(V) curve undervoltage 2 |
| 56 | V1L | 0.1V | According to specific regulatory requirements | Q(V) curve undervoltage 1 |
| 57 | V1H | 0.1V | According to specific regulatory requirements | Q(V) curve overvoltage 1 |
| 58 | V2H | 0.1V | According to specific regulatory requirements | Q(V) curve overvoltage 2 |
| 59 | ReactivePowerCMDTyp e |  | 0-7 | Reactive power command type 0 - unit power factor - - fixed PF - - default PF curve (American machine: Q(P)) - - custom PF curve - - capacitive reactive power percentage - inductive reactive power percentage - QV curve - QV_Dynamic |
| 60 | ActivePowerPercentCM D | % | 0-100 | Active power percentage set value |
| 61 | ReactivePowerPercentC MD | % | 0-60 | Reactive power percentage set value |
| 62 | PFCMD | 0.001 | 750-1000, 1750- 2000 | PF set value, 750-1000(under), 1750-2000(over) |
| 63 | PowerSoftStartSlope | ‰/min | 1-4000 | Loading rate, the percentage of power increase per minute. |
| 64 | ChargePowerPercentC MD | % | 0-100 | Charging power percentage setting |
| 65 | DischgPowerPercentCM D | % | 0-100 | Discharging power percentage setting |
| 66 | ACChgPowerCMD | % | 0-100 | AC charge percentage setting |
| 67 | ACChgSOCLimit | % | 0-100 | SOC limit setting for AC charging |
| 68 | ACChgStartHour | hour | 0-23 | AC charging start time - hour setting. |
|  | ACChgStartMinute | min | 0-59 | AC charging start time_minute setting |

| 69 | ACChgEndHour | hour | 0-23 | AC charging end time_hour setting |
| --- | --- | --- | --- | --- |
|  | ACChgEndMinute | min | 0-59 | AC charging end time_minute setting |
| 70 | ACChgStartHour1 | hour | 0-23 | AC charging start time_hour setting |
|  | ACChgStartMinute1 | min | 0-59 | AC charging start time_minutesetting |
| 71 | ACChgEndHour1 | hour | 0-23 | AC charging end time_hour setting |
|  | ACChgEndMinute1 | min | 0-59 | AC charging end time_minute setting |
| 72 | ACChgStartHour2 | hour | 0-23 | AC charging start time_hour setting |
|  | ACChgStartMinute2 | min | 0-59 | AC charging start time_minute setting |
| 73 | ACChgEndHour2 | hour | 0-23 | AC charging end time_hour setting |
|  | ACChgEndMinute2 | min | 0-59 | AC charging end time_minute setting |
| 74 | ChgFirstPowerCMD | % | 0-100 | Charging priority percentage setting |
| 75 | ChgFirstSOCLimit | % |  | Charging priority SOC limit setting |
| 76 | ChgFirstStartHour | hour | 0-23 | Charging priority start time_hour setting |
|  | ChgFirstStartMinute | min | 0-59 | Charge priority start time_min setting |
| 77 | ChgFirstEndHour | hour | 0-23 | Charging priority end time_hour setting |
|  | ChgFirstEndMinute | min | 0-59 | Charging priority end time_minute setting |
| 78 | ChgFirstStartHour1 | hour | 0-23 | Charging priority start time_hour setting |
|  | ChgFirstStartMinute1 | min | 0-59 | Charging priority start time_min setting |
| 79 | ChgFirstEndHour1 | hour | 0-23 | Charging priority end time_hour setting |
|  | ChgFirstEndMinute1 | min | 0-59 | Charging priority end time_minute setting |
| 80 | ChgFirstStartHour2 | hour | 0-23 | Charging priority start time_hour setting |
|  | ChgFirstStartMinute2 | min | 0-59 | Charging priority start time_minute setting |
| 81 | ChgFirstEndHour2 | hour | 0-23 | Charging priority end time_hour setting |
|  | ChgFirstEndMinute2 | min | 0-59 | Charging priority end |

|  |  |  |  | time_minut setting |
| --- | --- | --- | --- | --- |
| 82 | ForcedDischgPowerCM D | % | 0-100 | Forced discharge percentage setting |
| 83 | ForcedDischgSOCLimit | % | 0-100 | Forced discharge SOC limit setting |
| 84 | ForcedDischgStartHour | hour | 0-23 | Forced discharge start time_hour setting |
|  | ForcedDischgStartMinut e | min | 0-59 | Forced discharge start time_minute setting |
| 85 | ForcedDischgEndHour | hour | 0-23 | Forced discharge end time_hour setting |
|  | ForcedDischgEndMinute | min | 0-59 | Forced discharge end time_minute setting |
| 86 | ForcedDischgStartHour1 | hour | 0-23 | Forced discharge start time_hour setting |
|  | ForcedDischgStartMinut e1 | min | 0-59 | Forced discharge start time_minute setting |
| 87 | ForcedDischgEndHour1 | hour | 0-23 | Forced discharge end time_hour setting |
|  | ForcedDischgEndMinute 1 | min | 0-59 | Forced discharge end time_minute setting |
| 88 | ForcedDischgStartHour2 | hour | 0-23 | Forced discharge start time_hour setting |
|  | ForcedDischgStartMinut e2 | min | 0-59 | Forced discharge start time_minute setting |
| 89 | ForcedDischgEndHour2 | hour | 0-23 | Forced discharge end time_hour setting |
|  | ForcedDischgEndMinute 2 | min | 0-59 | Forced discharge end time_minute setting |
| 90 | EPSVoltageSet | 1V | 230,240, 277,208 ,220 | Off-grid output voltage level setting |
| 91 | EPSFreqSet | 1Hz | 50,60 | Off-grid output frequency system settings |
| 92 | LockInGridVForPFCurve | 0.1V | 2300-3000 | cosphi(P)lock in voltage |
| 93 | LockOutGridVForPFCurv e | 0.1V | 1500-3000 | cosphi(P)lock out voltage |
| 94 | LockInPowerForQVCurv e | % | 0-100 | Q(V) lock in power |
| 95 | LockOutPowerForQVCur ve | % | 0-100 | Q(V) lock out power |

|  | 96 | DelayTimeForQVCurve | Main period | 0-2000 | Q(V) delay |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | 97 | DelayTimeForOverFDer ate | Main period | 0-1000 | Overfrequency load reduction delay |  |
|  | 99 | ChargeVoltRef | 0.1V | 500-590 | Lead-acid battery charging specified voltage |  |
|  | 100 | CutVoltForDischg | 0.1V | 400-520 | Lead-acid battery discharge cut- off voltage |  |
|  | 101 | ChargeRate ChargeCurr | A | 0-140 | Charging current |  |
|  | 102 | DischgRate DischgCurr | A | 0-140 | Discharging current |  |
|  | 103 | MaxBackFlow | % | 0-100 | Feed-in grid power setting |  |
|  | 105 | EOD | % | 10%-90% | Cut SOC for discharging |  |
|  | 106 | TemprLowerLimitDischg | 0.1℃ | 0-65536 | Lead-acid Temperature low limit for discharging |  |
|  | 107 | TemprUpperLimitDischg | 0.1℃ | 0-65536 | Lead-acid Temperature high limit for discharging |  |
|  | 108 | TemprLowerLimitChg | 0.1℃ | 0-65536 | Lead-acid Temperature low limit for charging |  |
|  | 109 | TemprUpperLimitChg | 0.1℃ | 0-65536 | Lead-acid Temperature high limit for charging |  |
|  | 110 | FunctionEn1.ubPVGridO ffEn | Bit0 | 0,1 | 0 - disable 1 - enable, AC energy storage does not have this variable |  |
|  |  | FunctionEn1.ubFastZero Export | Bit1 |  | 0 - disable 1 - enable |  |
|  |  | FunctionEn1.ubMicroGr idEn | Bit2 |  | 0 - disable 1 - enable |  |
|  |  | FunctionEn1. ubBatShared | Bit3 |  | 0 - disable 1 - enable |  |
|  |  | FunctionEn1. ubChgLastEn | Bit4 |  | 0 - disable 1 - enable |  |
|  |  | FunctionEn1. CTSampleRatio | Bit5-6 |  | 0 :1/1000 1:1/3000 2:1/2000 For 12k: CTSampleRatioL2bit, Combine CTSampleRatioH2 bit to form a 4-bit CTSampleRatio 0：1/1000 1:1/3000 2:1/2000 3:1/4000 4:1/6000 |  |
|  |  | FunctionEn1. BuzzerEn | Bit7 |  | 0-disable 1-enable, only available for off-grid For 12k: DrycontactorCntl En |  |
|  |  | FunctionEn1. PVCTSampleType | Bit8-9 |  | For ACS3600: 0-PV power 1- SpecLoad For 12k :L2N CT reuse 0- no reuse 1- SpecLoad 2-ACCouple power |  |
|  |  | FunctionEn1. TakeLoadTogether | Bit10 |  | For off-grid: 0-disable 1- enable, for 12K : 0-ongrid disable 1- enable |  |
|  |  | FunctionEn1. OnGridWorkingMode | Bit11 2 | 5 / 41 | For 12K: consistant chk mask 0- disable 1-enable 0-self consumption 1-Charge First, only available for off-grid For 12K: consistantchk mask 0- |  |

#### 112

113

FunctionEn1. PVCTSampleRatio

FunctionEn1.GreenMod eEn

FunctionEn1.EcoModeE n

SetSystemType

SetComposedPhase

Bit12-13

Bit14

Bit15

Write only

0,1,2,3,4

Set 0

disable 1-enable

0 : 1/1000 1- 1/3000 2:1/2000

For 12k: CTSampleRatioL2bit, Combine CTSampleRatioH2 bit to form a 4-bit CTSampleRatio

0：1/1000 1:1/3000 2:1/2000

3:1/4000 4:1/6000

0-disable 1- enable, only available for off-grid

For 12K: AbsoluteZeroExport 0-disable 1- enable,

0-disable 1- enable, only available for off-grid

For 12K: 0-20ms 1-EPSRY on

ahead(10ms)

Set the single/parallel type

- no parallel (single one)

- Single-phase parallel operation forms a single-phase system. (Primary, which will not show on off-grid mode)

- Secondary (will not show on off-grid mode)

- Three phase parallel(Master) operation forms a three-phase

System

4-2*208(Master)

Option used for two split- phase inverter to make up a three-phase system

Clear the detected phases

| Write only | Set 1-3 | Set Composed phase 1-R 2-S 3-T |
| --- | --- | --- |
| Read only | Bit0-7 | Off-grid composed phases |
| Read only | Bit8-15 | On-grid detected phases |
|  | 1 | Parallel Alarm clear 1- clear |

| 114 | ClearFunction |
| --- | --- |
| 115 | OVFDerateStartPoint |
| 116 | PtoUserStartdischg |
| 117 | PtoUserStartchg |

0.01Hz

1W

1W

5000-5200

50W

-50W

Over-frequency load reduction start frequency point

Device starts discharging when Ptouser higher than this value

Device starts charging when Ptouser less than this value

#### 118

VbatStartDerating

0.1V

>CutVoltForDisc hg+2V

For lead-acid battery, according to given curve decrease discharging power when voltage lower than this value

#### 119

wCT_PowerOffset

26 / 41

1W	±1000W

signed short int; CT Power compensation, PtoUser direction is positive.

#### 120

stSysEnable.bit.HalfHou rACChrStartEn

stSysEnable.bit.ACCharg eType

Bit0

Bit1~3

0,1

0-5

- Disable，1-Enable； Default:0;

0-disable

- according to time 2-accoridng to voltage

- according to SOC

- according to Voltage and Time

- according to SOC and Time

For 12K:

  - - according to time

  - - according to SOC/Volt

  - - according to time with SOC/Volt

| stSysEnable.bit.DischgCt rlType | Bit4~5 | 0-2 | 0-according to voltage 1- according to SOC 2- according to both |
| --- | --- | --- | --- |
| stSysEnable.bit.OnGridE ODType | Bit6 | 0-1 | 0-according to voltage 1- according to SOC |

stSysEnable.bit. GenChargeType

Bit7

0-1

0-According to Battery voltage

1-According to Battery SOC

stSysEnable.bit.

SeparateZeroExportEn

Bit8

0-1

0-Disable(Default)，1-Enable

|  | 124 | OVFDerateEndPoint | 0.01Hz | 5000-5200 | Overfrequency load reduction ends at the frequency point |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | 125 | SOCLowLimitForEPSDisc hg | % | 0-EOD | SOC low limit for EPS discharge |  |
|  | 126 | OptimalChg_DisChg.Tim e0 | Bit0~1 | 0~2 | 0:00~0:30 Mark of time period charging and discharging. Default: 0; 0 - does not operate, 1-AC charge, 2-PV charge, 3 - discharge |  |
|  |  | OptimalChg_DisChg.Tim e1 | Bit2~3 | 0~2 | 0:30~1:00 Mark of time period charging and discharging. |  |
|  |  | OptimalChg_DisChg.Tim e2 | Bit4~5 | 0~2 | 1:00~1:30 Mark of time period charging and discharging. |  |
|  |  | …. |  |  |  |  |
|  |  | OptimalChg_DisChg.Tim e7 | Bit14~15 | 0~2 | 3:30~4:00 Mark of time period charging and discharging. |  |
|  | 127 | OptimalChg_DisChg.Tim e8 | Bit0~1 | 0~2 | 4:00~4:30 Mark of time period charging and discharging. Default: 0; 0 - does not operate, 1-AC charge, 2-PV charge, 3 - discharge |  |
|  |  | OptimalChg_DisChg.Tim e9 | Bit2~3 | 0~2 | 4:30~5:00 Mark of time period charging and discharging. |  |
|  |  | OptimalChg_DisChg.Tim e10 | Bit4~5 | 0~2 | 5:00~5:30 Mark of time period charging and discharging. |  |
|  |  | …. |  |  |  |  |
|  |  | OptimalChg_DisChg.Tim e15 | Bit14~15 | 0~2 | 7:30~8:00 Mark of time period charging and discharging. |  |

| 128 | OptimalChg_DisChg.Tim e16 | Bit0~1 | 0~2 | 8:00~8:30 Mark of time period charging and discharging. Default: 0; 0 - does not operate, 1-AC charge, 2-PV charge, 3 - discharge |
| --- | --- | --- | --- | --- |
|  | OptimalChg_DisChg.Tim e17 | Bit2~3 | 0~2 | 8:30~9:00 Mark of time period charging and discharging. |
|  | OptimalChg_DisChg.Tim e18 | Bit4~5 | 0~2 | 9:00~9:30 Mark of time period charging and discharging. |
|  | …. |  |  |  |
|  | OptimalChg_DisChg.Tim e23 | Bit14~15 | 0~2 | 11:30~12:00 Mark of time period charging and discharging. |
| 129 | OptimalChg_DisChg.Tim e24 | Bit0~1 | 0~2 | 12:00~12:30 Mark of time period charging and discharging. Default: 0; 0 - does not operate, 1-AC charge, 2-PV charge, 3 - discharge; |
|  | OptimalChg_DisChg.Tim e25 | Bit2~3 | 0~2 | 12:30~13:00 Mark of time period charging and discharging. |
|  | OptimalChg_DisChg.Tim e26 | Bit4~5 | 0~2 | 13:00~13:30 Mark of time period charging and discharging. |
|  | …. |  |  |  |
|  | OptimalChg_DisChg.Tim e31 | Bit14~15 | 0~2 | 17:00~17:30 Mark of time period charging and discharging. |
| 130 | OptimalChg_DisChg.Tim e32 | Bit0~1 | 0~2 | 16:00~16:30 Mark of time period charging and discharging. 0 - does not operate, 1-AC charge, 2-PV charge, 3 - discharge; |
|  | OptimalChg_DisChg.Tim e33 | Bit2~3 | 0~2 | 16:30~17:00 Mark of time period charging and discharging. |

|  | OptimalChg_DisChg.Tim e34 | Bit4~5 | 0~2 | 17:00~17:30 Mark of time period charging and discharging. |
| --- | --- | --- | --- | --- |
|  | …. |  |  |  |
|  | OptimalChg_DisChg.Tim e39 | Bit14~15 | 0~2 | 19:30~20:00 Mark of time period charging and discharging. |
| 131 | OptimalChg_DisChg.Tim e40 | Bit0~1 | 0~2 | 20:00~20:30 Mark of time period charging and discharging. 0-does not operate, 1-AC charge, 2-PV charge, 3 - discharge |
|  | OptimalChg_DisChg.Tim e41 | Bit2~3 | 0~2 | 20:30~21:00 Mark of time period charging and discharging. |
|  | OptimalChg_DisChg.Tim e42 | Bit4~5 | 0~2 | 21:00~21:30 Mark of time period charging and discharging. |
|  | …. |  |  |  |
|  | OptimalChg_DisChg.Tim e47 | Bit14~15 | 0~2 | 23:30~0:00 Mark of time period charging and discharging. |
| 132 | BatCellVoltLow | 0.1V | 0-200 | Battery cell voltage lower limit. |
|  | BatCellVoltHigh | 0.1V | 0-200 | Battery cell voltage upper limit |
| 133 | BatCellSerialNum | 1 | 0-200 | Number of battery cells in series |
|  | BatCellParaNum | 1 | 0-200 | Number of battery cells in parallel |
| 134 | UVFDerateStartPoint | 0.01Hz | 4500-5000 | Underfrequency load reduction starting point |
| 135 | UVFDerateEndPoint | 0.01Hz | 4500-5000 | The end point of underfrequency load reduction |
| 136 | OVFDerateRatio | %Pm/Hz | 1-100 | Underfrequency load ramp rate |
| 137 | SpecLoadCompensate | w | 0-65535 | The maximum amount of compensation for a specific load |
| 138 | ChargePowerPercentC MD | 0.1% | 0-1000 | Charging power percentage setting |
| 139 | DischgPowerPercentCM D | 0.1% | 0-1000 | Discharging power percentage setting |
| 140 | ACChgPowerCMD | 0.1% | 0-1000 | AC charge percentage setting |
| 141 | ChgFirstPowerCMD | 0.1% | 0-1000 | Charging priority percentage setting |

| 142 | ForcedDischgPowerCM D | 0.1% | 0-1000 | Forced discharge percentage setting |
| --- | --- | --- | --- | --- |
| 143 | ActivePowerPercentCM D | 0.1% | 0-1000 | Inverse active percentage setting |
| 144 | FloatChargeVolt | 0.1V | 500-560 | Float charge voltage |
| 145 | OutputPrioConfig |  | 0-3 | 0-bat first 1-PV first 2-AC first |
| 146 | LineMode |  | 0-2 | 0-APL(90-280V 20ms) 1-UPS (170-280V 10ms)2-GEN (90- 280V 20ms) |
| 147 | Battery capacity | Ah | 0-10000 | Battery capacity, for unmatched batteries |
| 148 | Battery nominal Voltage | 0.1V | 400-590 | Battery rating voltage, for unmatched batteries |
| 149 | EqualizationVolt |  | 500-590 | Battery equalization voltage |
| 150 | EqualizationInterval | Day | 0-365 | Balancing interval |
| 151 | EqualizationTime | hour | 0-24 | Balancing duration |
| 152 | ACFirstStartHour | hour | 0-23 | AC load start time_hours setting |
|  | ACFirstStartMinute | min | 0-59 | AC load start time _minutes setting |
| 153 | ACFirstEndHour | hour | 0-23 | AC load end time _hours setting |
|  | ACFirstEndMinute | min | 0-59 | AC load end ime_minutes setting |
| 154 | ACFirstStartHour1 | hour | 0-23 | AC load start time_hours setting |
|  | ACFirstStartMinute1 | min | 0-59 | AC load start time_minutes setting |
| 155 | ACFirstEndHour1 | hour | 0-23 | AC load end time_hours setting |
|  | ACFirstEndMinute1 | min | 0-59 | AC load end time_minutes setting |
| 156 | ACFirstStartHour2 | hour | 0-23 | AC load start time_Hours setting |
|  | ACFirstStartMinute2 | min | 0-59 | AC load start time_minutes setting |
| 157 | ACFirstEndHour2 | hour | 0-23 | AC load end time_hours setting |
|  | ACFirstEndMinute2 | min | 0-59 | AC load end time_minutes setting |
| 158 | ACChgStartVolt | 0.1V | 385-520 | Battery voltage of AC charging start, which will be valid after selecting ACChg according to voltage |
| 159 | ACChgEndVolt | 0.1V | 480-590 | Battery voltage of AC charging cut-off, effective after selecting ACChg according to voltage. |
| 160 | ACChgStartSOC | % | 0-90 | SOC of AC charging start , which will be valid after selecting ACChg according to SOC |

|  | 161 |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | 162 | BatLowVoltage | 0.1V | 400-500 | Battery under-voltage alarm point, which will be valid after selecting DisChgCtrl according to voltage or both voltage and time |  |
|  | 163 | BatLowBackVoltage | 0.1V | 420-520 | Battery under-voltage alarm recovery point, which will be valid after selecting DisChgCtrl according to voltage or bothvoltage and time |  |
|  | 164 | BatLowSOC | % | 0-90 | Battery under-voltage alarm point, which will be valid after selecting DisChgCtrl according to SOC or both SOC and time |  |
|  | 165 | BatLowBackSOC | % | 20-100 | Battery under-voltage alarm recovery point, which will be valid after selecting DisChgCtrl according to SOC or both SOC and time |  |
|  | 166 | BatLowtoUtilityVoltage | 0.1V | 444-514 | Voltage point for battery undervoltage to grid transfer, which will be valid after selecting DisChgCtrl according to voltage or both. |  |
|  | 167 | BatLowtoUtilitySOC | % | 0-100 | SOC for battery under-voltage to grid transfer, which will be valid after selecting DisChgCtrl according to SOC or both. |  |
|  | 168 | ACCharge Bat Current | A | 0-140 | Charge Current from AC |  |
|  | 169 | OngridEOD_Voltage | 0.1V | 400-560 | On-grid end of dischage voltage |  |
|  | ... |  |  |  |  |  |
|  | 171 | SOCCurve_BatVolt1 | 0.1V | 400-600 | Voltage point 1 for SOC calibration |  |
|  | 172 | SOCCurve_BatVolt 2 | 0.1V | 400-600 | Voltage point 2 for SOC calibration |  |
|  | 173 | SOCCurve_SOC1 | 1% | 0-100 | SOC reading based on Voltage point 1 |  |
|  | 174 | SOCCurve_SOC2 | 1% | 0-100 | SOC reading based on Voltage point 2 |  |
|  | 175 | SOCCurve_InnerResistance | mΩ | 0-100 | Inner resistance of the battery |  |
|  | 176 | MaxGridInputPower | W |  | Max. Grid import power limitation |  |
|  | 177 | GenRatePower | W |  | The rated power of generator input |  |
|  | 179 | uFunctionEn2.ACCTDire ction | Bit0 | 0,1 | 0-Normal 1-Reversed |  |
|  |  | uFunctionEn2.PVCTDire ction | Bit1 | 0,1 | 0-Normal 1-Reversed |  |
|  |  | uFunctionEn2.AFCIAlar mClr | Bit2 | 0,1 | 0-null 1-clear For ACS 0-single phase compensation ，1-three phase compensation |  |
|  |  | uFunctionEn2.BatWake upEn PVSellFirst | Bit3 | 0,1 | 0-Disable 1-Enable |  |

|  | uFunctionEn2.VoltWatt En | Bit4 | 0,1 | 0-Disable 1-Enable |
| --- | --- | --- | --- | --- |
|  | uFunctionEn2.TriptimeU nit | Bit5 | 0,1 | 0-Disable 1-Enable |
|  | uFunctionEn2.ActPower CMDEn | Bit6 | 0,1 | 0-Disable 1-Enable |
|  | uFunctionEn2.ubGridPe akShaving | Bit7 | 0,1 | 0-Disable 1-Enable |
|  | uFunctionEn2.ubGenPe akShaving | Bit8 | 0,1 | 0-Disable 1-Enable |
|  | uFunctionEn2.ubBatChg control | Bit9 | 0,1 | 0-SOC,1-Volt |
|  | uFunctionEn2.ubBatDisc hgControl | Bit10 | 0,1 | 0-SOC,1-Volt |
|  | uFunctionEn2.ubACcou pling | Bit11 | 0,1 | 0-Disable 1-Enable |
|  | uFunctionEn2.ubPVArcE n | Bit12 | 0,1 | 0-Disable 1-Enable |
|  | uFunctionEn2. ubSmartLoadEn | Bit13 | 0,1 | 0-Generator 1-Smart Load |
|  | uFunctionEn2.ubRSDDis able | Bit14 | 0,1 | 0-Enable 1-Disable |
|  | uFunctionEn2.OnGridAl waysOn | Bit15 | 0,1 | 0-Disable 1-Enable |
| 180 | AFCIArcThreshold |  |  |  |
| 181 | VoltWatt_V1 | 0.1V |  | 1.05Vn-1.09Vn, default1.06Vn |
| 182 | VoltWatt_V2 | 0.1V |  | (V1+0.01Vn)-1.10Vn, default1.1Vn |
| 183 | VoltWatt_DelayTime | Main cnt | 500-60000ms | Default 10000ms |
| 184 | VoltWatt_P2 | % | 0-200 |  |
| 185 | Vref_QV | 0.1V |  |  |
| 186 | Vref_filtertime | s | 300-5000 |  |
| 187 | Q3_QV | % |  |  |
| 188 | Q4_QV | % |  |  |
| 189 | P1_QP | % |  |  |
| 190 | P2_QP | % |  |  |
| 191 | P3_QP | % |  |  |
| 192 | P4_QP | % |  |  |
| 193 | UVFIncreaseRatio | %Pm/Hz | 1-100 | Underfrequency load ramp rate |
| 194 | GenChgStartVolt | 0.1V | 384-520 | Intitial voltage for generator charging the battery, which will |

Shenzhen Lux Power Technology Co., Ltd	www.luxpowertek.com

|  |  |  |  | be valid after selecting GenChg according to voltage. |
| --- | --- | --- | --- | --- |
| 195 | GenChgEndVolt | 0.1V | 480-590 | Battery voltage at the end of generator charging, which will be valid after selecting GenChg according to voltage. |
| 196 | GenChgStartSOC | % | 0-90 | SOC limit for generator charging the battery, which will be valid after selecting charge according to SOC |
| 197 | GenChgEndSOC | % | 20-100 | SOC limit to end thegenerator charging, which will be valid after selecting charge according to SOC |
| 198 | MaxGenChgBatCurr | A | 0-4000 | Max. Charge current from generator |
| 199 | OverTempDeratePoint | 0.1℃ | 600-900 | Overtemperature load reduction point |
| 201 | ChgFirstEndVolt | 0.1V | 480-590 | Charging priority voltage limit |
| 202 | ForceDichgEndVolt | 0.1V | 400-560 | Forced discharge voltage limit |
| 203 | GridRegulation |  |  | Grid regulation settings |
| 204 | LeadCapacity | Ah | 50-5000 | Capacity of the lead acid battery |
| 205 | GridType |  |  | 0-Split240V/120V 1-3phase 208V/120V - Single 240V - Single 230V - Split 200V/100V |
| 206 | GridPeakShavingPower | 0.1kw | 0-255 |  |
| 207 | GridPeakShavingSOC | % | 0-100 |  |
| 208 | GridPeakShavingVolt | 0.1V | 480-590 |  |
| 209 | PeakShavingStartHour | hour | 0-23 | PeakShaving start time_Hour setting |
|  | PeakShavingStartMinut e | min | 0-59 | PeakShaving start time_minutes setting |
| 210 | PeakShavingEndHour | hour | 0-23 | PeakShaving end time_hours setting |
|  | PeakShavingEndMinute | min | 0-59 | PeakShaving end time_minutes setting |
| 211 | PeakShavingStartHour1 | hour | 0-23 | PeakShaving sttart ime_hours setting |
|  | PeakShavingStartMinut e1 | min | 0-59 | PeakShaving start time_minutes setting |
| 212 | PeakShavingEndHour1 | hour | 0-23 | PeakShaving end time_ hours |

|  |  |  |  |  | setting |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | PeakShavingEndMinute 1 | min | 0-59 | PeakShaving end time_minutes setting |  |
|  | 213 | SmartLoadOnVolt | 0.1V | 480-590 |  |  |
|  | 214 | SmartLoadOffVolt | 0.1V | 400-520 |  |  |
|  | 215 | SmartLoadOnSOC | % | 0-100 |  |  |
|  | 216 | SmartLoadOffSOC | % | 0-100 |  |  |
|  | 217 | StartPVpower | 0.1kW | 0-120 |  |  |
|  | 218 | GridPeakShavingSOC1 | % | 0-100 |  |  |
|  | 219 | GridPeakShavingVolt1 | 0.1V | 480-590 |  |  |
|  | 220 | ACCoupleStartSOC | % | 0-100 |  |  |
|  | 221 | ACCoupleEndSOC | % | 0-255 |  |  |
|  | 222 | ACCoupleStartVolt | 0.1V | 400-595 |  |  |
|  | 223 | ACCoupleEndVolt | 0.1V | 420-800 |  |  |
|  | 224 | LCDVersion | But0~7 | 0-255 |  |  |
|  |  | LCDScreenType | Bit8 | 0-1 | 0-screen of B size 1-screen of S size |  |
|  |  | LCDODM | Bit9~15 | 0-127 | See LCD Definition Table |  |
|  | 225 | LCDPassword |  | 0~65535 | Password for LCD Advanced page |  |
|  | 227 | BatStopChgSOC | % | 10-101 | When battery SOC reaches set value , inverter will stop charging the battery , and when the battery SOC < = (Set value -5), inverter will return charging the battery |  |
|  | 228 | BatStopChgVolt | 0.1V | 400-595 | When battery Voltage reaches set value , inverter will stop charging the battery , and when the battery Volt < = (Set value - 20 ), inverter will return charging the battery |  |
|  | 230 | unMeterCfg.MetersNum | Bit0~3 | 0-15 | Meter Numbers |  |
|  |  | RSVD0 | Bit4~7 |  |  |  |
|  |  | unMeterCfg.MeterMeasureType | Bit8 | 0,1 | - Meter1(Addr=1)measure AC Meter2(Addr=2)measure PV - reversed |  |
|  |  | unMeterCfg.InstallPhase | Bit9~10 | 0-3 | 0-R phase，1-S phase，2-T phase，ensure the Install Phases of all meters are the same ，(only valid for 3phase meter) |  |
|  |  | RSVD1 | Bit11~12 | 0-3 |  |  |
|  |  | RSVD2 | Bit13~15 |  | RVSD |  |
|  | 231 | unResetRecord.bit.G100 | Bit0 | 0,1 | 1-Reset the G100 lockout state |  |
|  |  | unResetRecord.bit.Rsvd |  |  | RVSD |  |
|  | 232 | GridPeakShavingPower1 | 0.1kW | 0-255 |  |  |

|  | 233 | uFunction4En. ubQuickChgStartEn | Bit0 | 0,1 |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | uFunction4En. ubBattBackupEn | Bit1 | 0,1 |  |  |
|  |  | uFunction4En. ubMaintenaceEn | Bit2 | 0，1 | 1-Enable， Once enabled ,andif battery is detected to be never got charged fully within 30days ，then battery will get fully charged from grid at 23：00 of the last day of 30days duration |  |
|  |  | uFunction4En.ubWorkingMode | Bit3 | 0，1 | 0：arranging the work mode 1 for a 7-days time period 1：arranging the work mode 2 for a 7-days time period |  |
|  |  | uFunction4En.ubDryContactorMultiplex | Bit4-7 |  | - - null - - RSD - - Dark Start - - Smart load - - Non-critical Load |  |
|  |  | uFunction4En.ubExCTPosition | Bit8-9 |  | 0-GridtoUser 1-InvGridPort |  |
|  |  | uFunction4En.ubOverFreq_fstop | Bit10 | 0，1 | 0：deactivated , 1：activated |  |
|  | 234 | QuickChgTime | min |  |  |  |
|  | 235 | uwNoFullChgDay | Bit0~Bit7(Read only ) | 0~255 | Days counter since the last time that battery SOC>=99 |  |
|  |  | uwNoFullChgDayNumSet | Bit8~Bit15 | 0~255 | Calibration period (Days) from the last time that battery SOC< 99 |  |
|  | 236 | FloatChgThreshold | 0.01C | 1-255 | When charge current in CV getting lower than this setting, switch to float charge |  |
|  | 237 | GenCoolDownTime | 0.1min | 1-255 | Gen cool down time when dry contactor is off |  |
|  | 241 | Permit Service |  |  | 0-disable , non 0-enable |  |
|  | 242 | uwNPEThreshold | 0.1V | 0-65535 | Zero ground detection voltage range setting value |  |
|  | 243 | ... |  |  |  |  |
|  | 244 | Bootloader_Version | Bit0-7 | 0-255 | Bootloader Version |  |
|  |  | Bootloader_UpdateFlag | Bit8-15 |  |  |  |
|  | 245 | FlashSize |  | 0-65535 |  |  |
|  | 248 | WattNode uwCtAmps1 | A | 0-6000 | CT1 ratio of wattnode meters |  |
|  | 249 | WattNode uwCtAmps2 | A | 0-6000 | CT2 ratio of wattnode meters |  |
|  | 250 | WattNode uwCtAmps3 | A | 0-6000 | CT3 ratio of wattnode meters |  |
|  | 251 | WattNode uwCtDirections1 | Bit0 | 0,1 | CT1 direction of wattnode meter |  |
|  |  | WattNode uwCtDirections2 | Bit1 | 0,1 | CT2 direction of wattnode meter |  |
|  |  | WattNode uwCtDirections3 | Bit2 | 0,1 | CT3 direction of wattnode meter |  |
|  |  | WattNode_UpdateFrequency | Bit3~5 | 0~7 | 0 - 1S 1 - 5S 2 - 20S 3 - 60S 4 - 100 ms 5- 200ms 6- 500 ms |  |
|  |  | Resvd | Bit6~15 | … | … |  |
|  | 252 | NEC120BusBarLimit | A |  | For NEC 120% Rule |  |
|  | 253 | DeltaSOC | % | 5~80 | SOC hysteresis, only set lower limit, to be improved |  |
|  | 254 | DeltaVolt | 0.1V | 20~100 | Volt hysteresis, only set lower limit, to be improved |  |
|  | 256 | GenStartHour | hour | 0-23 | Generator start time_Hour setting |  |
|  |  | GenStartMinute | min | 0-59 | Generator start time_minutes setting |  |
|  | 257 | GenEndHour | hour | 0-23 | Generator end time_hours setting |  |
|  |  | GenEndMinute | min | 0-59 | Generator end time_minutes setting |  |
|  | 258 | GenStartHour1 | hour | 0-23 | Generator start time_Hour setting |  |
|  |  | GenStartMinute1 | min | 0-59 | Generator start time_minutes setting |  |
|  | 259 | GenEndHour1 | hour | 0-23 | Generator end time_hours setting |  |

|  |  |  |  | Generator end time_minutes |
| --- | --- | --- | --- | --- |
|  | GenEndMinute1 | min | 0-59 | setting |
| 260 | uwBusVoltHightSet | 1 V | 550-595 | BUS overvoltage point alarm voltage setting value |
|  |  |  |  | Battery discharge recovery threshold |
| 261 | bDisRecovSocThresh | % | Min:5% | ：SOC |
|  |  |  |  | Battery discharge recovery threshold |
|  | bDisRecovVoltThresh | 0.1V | Min:1V | ：Volt |

Table 8 Hold register mapping table

# Appendix

### Definition of the operation mode of on/off-grid energy storage all in one machine.

| Status code | Device work status | Remark |
| --- | --- | --- |

| 0x00 | Standby |  |
| --- | --- | --- |
| 0x01 | Fault |  |
| 0x02 | Programming |  |
| 0x04 | PV PV connected to grid | PV power feed back to grid, AC energy storage does not have this variable. |
| 0x08 | PV PV charging | PV power charge the battery, AC energy storage does not have this variable. |
| 0x0C | PV charging connected to the grid | A portion of the PV power is used for battery charging, while another portion is used for feeding back to grid, and AC energy storage does not have this variable. |
| 0x10 | The battery connect to the grid | The power od battery discharging will feed back to grid |
| 0x14 | (PV+ battery) connected to the grid | Battery discharge and PV energy are connected to the grid together, and AC energy storage does not have this variable |
| 0x20 | AC charging | Grid charges the battery |
| 0x28 | (PV+AC) charging | PV and grid power charge the battery together, and AC energy storage does not have this variable. |
| 0x40 | The battery is off-grid | off-grid mode, battery discharge |
| 0x60 | Off-grid + battery charging | On-grid system charge the battery (AC Coupled) |
| 0x80 | PV off-grid | PV power fluctuates randomly, the off-grid output is unstable, and the inverter is prohibited from working in this state, and AC energy storage does not have this variable. |
| 0xC0 | (PV+ battery) off-grid | In 0ff-gird mode, PV power and battery discharge, AC energy storage does not have this variable. |
| 0x88 | PV charging + off-grid | A portion of the PV power is used for off-grid output, while another portion is used for battery charging, and AC energy storage does not have this variable. |

Table 9 Operational mode definitions

### Fault and Alarm Code Definitions

| Bit0-31 | Fault information | Fault Code | Warning information | Warning Code |
| --- | --- | --- | --- | --- |
| 0 | Internal communication failure 1 | E000 | Battery communication failed | W000 |
| 1 | Model fault | E001 | AFCI communication failure | W001 |
| 2 | rsvd | E002 | AFCI High Battery low temperature AFCI High | W002 |
| 3 | rsvd | E003 | Meter communication failed | W003 |
| 4 | rsvd | E004 | The battery cannot be | W004 |

Shenzhen Lux Power Technology Co., Ltd	www.luxpowertek.com

35 / 41

|  |  |  |  | charged and discharged |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | 5 | rsvd | E005 | The automated test failed | W005 |  |
|  | 6 | rsvd | E006 | RSD Active | W006 |  |
|  | 7 | rsvd | E007 | LCD communication failure | W007 |  |
|  | 8 | Parallel CAN communication failure | E008 | Software version mismatch | W008 |  |
|  | 9 | The host is missing | E009 | The fan is stuck and not rotating | W009 |  |
|  | 10 | The rated power output of multiple hosts or parallel machines is inconsistent 8-12K:Inconsistent rated power output for grid connection Trip6-20k:Inconsistent rated power output for grid connection | E010 | Rsvd Trip6-20k: Grid overload | W010 |  |
|  | 11 | The AC of the parallel system is inconsistent or the safety settings of the parallel system are inconsistent 8-12K:Inconsistent parallel machine safety regulations Trip6-20k:Inconsistent parallel machine safety regulations | E011 | The number of secondary units for parallel operation exceeds the Limit Trip6-20k:Rsvd | W011 |  |
|  | 12 | UPS short circuit | E012 | Battery reverse MOS becomes abnormal 8-12k:The parallel system is experiencing phase loss Trip6-20k:The parallel system is experiencing phase loss | W012 |  |
|  | 13 | UPS reverse current | E013 | Temperature of the radiator is out of range 8-12k:The parallel system does not have a designated primary unit Trip6-20k:The parallel system does not have a designated primary unit | W013 |  |
|  | 14 | BUS short circuit | E014 | Set up multiple hosts in the parallel system | W014 |  |
|  | 15 | The phase of the three-phase parallel system is abnormal | E015 | Battery reverse | W015 |  |
|  | 16 | Relay failure | E016 | No grid connection | W016 |  |
|  | 17 | Internal communication failure 2 | E017 | The grid voltage exceeds the specified range | W017 |  |
|  | 18 | Internal communication failure 3 | E018 | The grid frequency exceeds the specified range | W018 |  |
|  | 19 | BUS overvoltage | E019 | rsvd | W019 |  |
|  | 20 | EPS connection fault | E020 | The insulation resistance is low, and AC energy storage does not have this variable | W020 |  |
|  | 21 | PV overvoltage, AC energy storage without this fault | E021 | The leakage current is too high | W021 |  |

- Overcurrent protection

- Neutral fault

- PV short circuit, AC energy storage has no such fault

- Heatsink temperature out of

range

- Internal failure

E022 E023 E024

E025 E026

DCI exceeded the standard

PV short circuit, AC energy storage does not have this variable

Rsvd

Trip6-20k:GFCI module failure

Battery overvoltage Battery undervoltage

W022 W023 W024

W025 W026

| 27 | Consistency failure | E027 | Battery open circuit | W027 |
| --- | --- | --- | --- | --- |
| 28 | The generator connection in parallel system is inconsistent | E028 | EPS overload | W028 |
| 29 | Parallel synchronization triggers signal loss | E029 | EPS voltage high | W029 |
| 30 | rsvd | E030 | Meter reversed | W030 |
| 31 | Internal communication failure 4 | E031 | DCV exceeded the standard | W031 |

Table 10 Fault and alarm definitions

| FaultCode | Fault decription | LCD display | Trouble shooting |
| --- | --- | --- | --- |
| E000 | Internal communication fault1 | E000 | Restart inverter, if the error still exist, contact us (DSP&M3) |
| E001 | Model fault | E001 | Reset model, check if safety standard switch is at the right place |
| E002 | rsvd | E002 |  |
| E003 | rsvd | E003 |  |
| E004 | rsvd | E004 |  |
| E005 | rsvd | E005 |  |
| E006 | rsvd | E006 |  |
| E007 | rsvd | E007 |  |
| E008 | Parallel CAN communication failure | E008 | Check CAN cable connection |
| E009 | The host is missing | E009 | Check parallel setting |
| E010 | Muti Master units in parallel system 8-12KW : Para Rating Watt Diff Inverters are with different power rating configurations | E010 | Check parallel setting |
| E011 | Inconsistent AC connection 8-12k: grid safety settings in parallel computing systems. | E011 | Check parallel connection Check parallel setting |
| E012 | UPS | E012 | Check parallel connection or contact us |

|  | UPS short circuit |  |  |
| --- | --- | --- | --- |
| E013 | UPS UPS backfilling | E013 | Restart inverter, if the error still exist, contact us |
| E014 | BUS BUS short circuit | E014 | Contact us |
| E015 | Phase abnormality in a three-phase parallel system | E015 | Check parallel connection and setting |
| E016 | Relay fault | E016 | Restart inverter, if the error still exist, contact us |
| E017 | Internal communication fault2 | E017 | Restart inverter, if the error still exist, contact us (DSP&M8) |
| E018 | Internal communication fault3 | E018 | Restart inverter, if the error still exist, contact us (DSP&M3) |
| E019 | Bus voltage high | E019 | Check PV input connection |
| E020 | EPS connection fault | EPS CN Fault | Check EPS and AC connection |
| E021 | PV voltage high | PV voltage high | Check PV input connection |
| E023 | Neutral fault | Neutral fault | Check neutral connection |
| E024 | PV short | E024 | Check PV connection |
| E025 | Temperature over range | NTC Open | Check NTC connection |
| E026 | Internal Fault | E026 | Restart inverter, if the error still exist, contact us (Bus sample) |
| E027 | Sample inconsistant between main and slave CPU | E027 | Restart inverter, if the error still exist, contact us |
| E028 | SNA 3000-6000: sync signal lost in parallel system ; The parallel synchronization signal is lost 8-12KW :Para Gen connection unAccord; the generator connection is abnormal | E028 | Check CAN cable connection Check Gen connection |
| E029 | sync triger signal lost in parallel system. Parallel synchronization triggers signal loss | E029 | Check CAN cable connection |
| E030 | rsvd | E030 |  |

| E031 | Internal communication fault4 | E031 | Restart inverter, if the error still exist, contact us (DSP&M8) |
| --- | --- | --- | --- |

Table 11 Failure Information Table

| WarningCode | Warning decription | LCD display | Trouble shooting |
| --- | --- | --- | --- |
| W000 | Communication failure with battery | Batery Com Fault | Check communication cable, if the warning still exist, contact us |
| W001 |  |  |  |
| W002 |  |  |  |
| W003 | Communication failure with meter | Meter Com Fault | Check communication cable, if the warning still exist, contact us |
| W004 | Battery failure | Battery failure | Restart battery, if the warning still exist, contact us |
| W005 | AutoTest failure | AutoTest failure | Restart inverter, if the error still exist, contact us |
| W006 |  |  |  |
| W007 | LCD communication Fault | W007 | Restart battery, if the warning still exist, contact us |
| W008 | Software mismatch | W008 |  |
| W009 | Fan Stuck | W009 | Restart inverter, if the error still exist, contact us |
| W010 | Same para address | W010 |  |
| W011 | Secondary overflow | W011 | Check parallel number |
| W012 | BatOnMos 8-12KW：Phase loss for parallel system | W012 | Restart inverter, if the error still exist, contact us |
| W013 | Overtemprature 8-12KW：No primary set in parallel system | W013 | Restart inverter(or check parallel setting), if the error still exist, contact us |
| W014 | 8-12KW：Muti- Primary set in parallel system | W014 | Check parallel setting |
| W015 | Battery Reverse | W015 | Check battery input polarities(available for SNA unit) |
| W016 | No AC Connection | No AC Connection | Check AC Connection |
| W017 | AC Voltage out of range | AC V Outrange | Check AC voltage |
| W018 | AC Frequency out of range | AC F Outrange | Check AC frequency |
| W019 | AC inconsistent in parallel system2 The parallel AC is inconsistent | W019 | Check parallel connection or contact us |

| W020 | PV Isolation low | PV Isolation low | Restart inverter, if the error still exist, contact us |
| --- | --- | --- | --- |
| W021 | Leakage I high | Leakage I high | Restart inverter, if the error still exist, contact us |
| W022 | DC injection high | DC injection high | Restart inverter, if the error still exist, contact us |
| W023 | PV short circuit | PV short | Check PV input connection |
| W024 |  |  |  |
| W025 | Battery voltage high | Bat Volt High | Check battery connection |
| W026 | Battery voltage low | Bat Volt Low | Check battery connection |
| W027 | Battery open | Battery open | Check battery connection |
| W028 | EPS Overload | EPS Over load | Check EPS load |
| W030 | Meter Reversed | W030 | Check meter connection |
| W031 | EPS DCV high | W031 | Restart inverter, if the error still exist, contact us |

Table 12 Alarm information table

### On-grid Regulatory Mapping Table

| Bit0-31 | Type of safety | Remark | American model voltage system Safety type |
| --- | --- | --- | --- |
| 0 | General | Same VDE0126 | UL1741&IEEE1547 |
| 1 | VDE0126 | Germany | Hawaii （HECO） |
| 2 | AS4777 | Australia | USA(rule21) |
| 3 | NEWZEALAND | New Zealand | PR-LUMA |
| 4 | CGC | China | KIUC |
| 5 | G59 | United Kingdom |  |
| 6 | G83 | United Kingdom |  |
| 7 | N4105 | Germany |  |
| 8 | CEI0-21 | Italy |  |
| 9 | EN50438 |  |  |
| 10 | EN50438_Finl and | Finland |  |
| 11 | Japan | Japan |  |
| 12 | PEA | Thailand |  |
| 13 | MEA | Thailand |  |

| 14 | EN50438_Irela nd | Ireland |  |
| --- | --- | --- | --- |
| 15 | Czech | Czech Republic |  |
| 16 | South Africa | South Africa |  |
| 17 | Barbadors | Barbadors |  |
| 18 | CEI021ARETI |  |  |
| 19 | EN50549 |  |  |
| 20 | Denmark | Denmark |  |
| 21 | Poland | Poland |  |
| 22 | Spain | Spain |  |
| 23 | C10/C11 | Belgium |  |
| 24 | TOR | Austria |  |
| 25 | Denmark-2 | Denmark(DK2) |  |
| 26 |  |  |  |
| 27 |  |  |  |
| 28 |  |  |  |
| 29 |  |  |  |
| 30 |  |  |  |
| 31 |  |  |  |

Table 13: on-grid regulatory mapping table

### LCD Definition Table

| Code | Definition |  |
| --- | --- | --- |
|  | Brand | Machine type |
| LCD0 | Luxpowertek | LXP-LB-8-12K |
| LCD1 | EG4 | LXP-LB-8-12K |
| LCD2 | CROWN | LXP-LB-8-12K |
| LCD3 | EG4 MINUS | LXP-LB-8-12K |
| LCD4 | Luxpowertek | 10K |
| LCD5 | EG4 | 10K |
| LCD6 | CROWN | 10K |
| LCD7 | Luxpowertek | 100K |
| LCD8 | Luxpowertek | 6-20K |
| LCD9 | EG4 | 6-20K |
| LCD10 | CROWN | 6-20K |
| LCD11 | Luxpowertek | Trip_LV |
| LCD12 | Luxpowertek | GEN3-6K |
| LCD13 | EG4 | GEN3-6K |
| LCD14 | CROWN | GEN3-6K |
| LCD15 | ... | ... |
| LCD16 | Luxpowertek | GEN7-10K |
| LCD17 | EG4 | GEN7-10K |
| LCD18 | CROWN | GEN7-10K |
| LCD19 | ... | ... |
| LCD20 | Luxpowertek | SNA |
| LCD21 | EG4 | SNA |
| LCD22 | CROWN | SNA |
| RSVD | ... | ... |